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June 3, 2026

Lisa, I have reviewed the site plan for the Daytop Application, and I have some questions and concerns. 

1. The hot box needs to be labeled at the entrance to the property 

2. Where are the main shutoffs for the sprinkler systems for each of the buildings? 

3. This is a request that I would like consideration on; A number of the parking areas behind the buildings are extremely tight in regard to space. They also have only one means of entry and egress.  Could there be a possibility of having gated access to the other end of each of these dead ends that could utilize pavers and a access gate to allow fire apparatus to get to the rear of these buildings?  

This would prevent residents from using the area but allow fire access. 

4. Tower access road- what is the width and surface of this road? 

5. Hydrants- I see the 4 yard hydrants at the four corners of the proposed site, but where are the locations of the other hydrants needed for the site?  Approximate to the buildings. 
These are a few of the questions I have regarding the site and I reserve the right to further review the plans as the project moves forward. 

Thank you for the opportunity to review these plans. 

Tom Ryan, Fire Official
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